## Electrical
TM39: Electrical meter commissioning checklist
Pre-commissioning checks
Verify meter specification | Yes/No | Comments
Confirm the meter type (whole current or CT, single-phase, three-phase, smart, digital)
Check the voltage and current ratings
Confirm the accuracy class
Inspect meter and accessories | Yes/No | Comments
Check the meter for any physical damage
Verify accessories (current transformers, voltage transformers, connectors) are correct and compatible
Site readiness | Yes/No | Comments
Confirm that the metering location is clean, dry, and accessible
Ensure that the mounting structure/enclosure is ready and secure
Safety precautions | Yes/No | Comments
Ensure all personnel wear appropriate PPE, as stated in the RAMS
Disconnect power supply before starting installation
Confirm earthing and bonding arrangements
Installation
Mounting | Yes/No | Comments
Install the meter firmly in the designated enclosure or panel
Ensure the meter is mounted upright and securely
Wiring | Yes/No | Comments
Connect the line, load, neutral, and earth wires according to wiring diagram
For three-phase meters, ensure correct phase sequence
Use appropriate wire sizes and torque specifications
CT and PT connections | Yes/No | Comments
Connect current transformers (CTs) and potential transformers (PTs) correctly, observing polarity
Check the CT secondary circuit is never open under load
Power up and initial testing
Switch power ON | Yes/No | Comments
Apply power supply to the meter
Check for abnormal signs such as smoke, sparks, or noise
Initial meter check | Yes/No | Comments
Check that CT and VT ratio is correct in the meter settings
Verify the meter display powers up and shows basic parameters
Confirm correct phase sequence and voltage readings
Test CT and PT connections | Yes/No | Comments
Check secondary circuits of CT/PT for correct polarity and operation Note: for a pre-wired panel, if these are incorrect, it should be raised for correction
Check meter functionality | Yes/No | Comments
Verify energy measurement (kW·h/kVA·h) by applying a known load
Confirm meter starts recording consumption correctly
Calibration and verification
Accuracy testing | Yes/No | Comments
Compare meter readings with a calibrated reference meter, ideally over a week as some errors do not appear immediately
Perform load tests at different current levels: minimum, nominal, maximum (where practicable; could be difficult on large supplies)
Calibration | Yes/No | Comments
If required, calibrate the meter according to manufacturer instructions or utility standards
Record results | Yes/No | Comments
Document initial readings, test results, and calibration certificates
Sealing and security | Yes/No | Comments
Seal the meter enclosure after wiring to prevent tampering
Label the meter with ID, installation date, and circuit details
Commissioning completion
Final inspection | Yes/No | Comments
Inspect all connections, seals, and labelling
Ensure safety and compliance with relevant standards
Documentation | Yes/No | Comments
Complete commissioning report with meter details, test results and photos Note: pre-wired panels, include manufacturer certificates that meters have been tested and proven correct as installed
Handover | Yes/No | Comments
Provide meter information and instructions to the end user or facility manager
Ensure each meter password has been changed from the default settings and documented
Train personnel on meter reading and basic troubleshooting if needed
Post-commissioning
Monitoring | Yes/No | Comments
Monitor meter readings periodically for consistency
Address any anomalies immediately
Routine maintenance | Yes/No | Comments
Schedule periodic inspections and cleaning
Plan for periodic recalibration as per standards

## Natural Gas
TM39: Gas meter commissioning checklist
Pre-installation checks | Yes/No | Comments
Approved meter model and specification confirmed
Meter installation drawing reviewed and approved
Meter location matches approved drawings
Access to meter is safe and compliant
Gas supply isolated and lock-out/tag-out (LOTO) applied
Pipework cleaned, pressure tested, and purged
Correct orientation of meter (flow direction)
Suitable environmental conditions (temperature, ventilation)
Adequate clearance for maintenance and reading
Installation checks | Yes/No | Comments
Meter securely mounted and supported
Correct pipe size and fittings installed
Approved sealing and gaskets used
Isolation valves installed upstream and downstream
No mechanical strain on meter body
Leak test performed (soap test or pressure drop)
Gas tightness verified
Meter index (reading) recorded at commissioning
Electrical/communications checks (if applicable) | Yes/No | Comments
Pulse output connected correctly
Communication wiring checked (Modbus, M-Bus, LoRa, etc.)
Cable terminations tight and labelled
Signal polarity verified
Communication tested with BMS / data logger
Meter address and baud rate configured
Data reading matches manual reading
Functional checks | Yes/No | Comments
Meter responds to gas flow (index increases)
Flow direction verified
Pressure drop across meter acceptable
Reading consistency checked against reference meter (if applicable)
Alarm functions tested (if any)
Calibration and documentation | Yes/No | Comments
Calibration certificate valid and traceable
Serial numbers recorded
Commissioning report completed
Ensure each meter password has been changed from the default settings and documented.
'As built' drawings updated
O&M manuals provided
Site representative sign-off obtained

## Thermal
TM39: Thermal meter commissioning checklist
Installation | Yes/No | Comments
Install meter according to serial number and location
Confirm installed parts are in line with manufacturer’s requirements, including meter location in pipework and associated pockets
Install validation temperature probe pockets and orifice plates
Communications | Yes/No | Comments
Address meter and commission comms to head end
From the heat meter’s LCD display, record: flow rate, volume, flow temp, return temp, kW·h, and kW, along with the date and time the reading was taken
Check that manual meter readings match those recorded electronically
Set meter logging to required interval
Verification | Yes/No | Comments
Verify installation of water meter, calculator and flow/return probe locations
Record the flow temperature from the heat meter display; validate against a calibrated handheld immersion probe
Record the return temperature from the heat meter display; validate against a calibrated handheld immersion probe
Record the flow rate from the heat meter display; validate against a calibrated handheld flow meter connected to the validation orifice plate
Include meter calibration certification with installation documentation
Record kW·h, kW display readings
Witness sign-off; ensure each meter password has been changed from the default settings and documented
Billing | Yes/No | Comments
Commission data transfer from comms head end to the billing and analytics system
Validate data passage from meter to billing system
Verification by calculation — do the sub meters add to the main meters? If not, return to previous steps
Trend review and reporting — do the meter profiles seem sensible? If not return to previous steps
Data analytics set up and testing
Revert logging to specified interval
Documentation | Yes/No | Comments
A single coordinated document pack will be used by all trades
Format set by lead contractor, each trade can enhance their section with additional company-specific checklists
The first contractor will start the chain, passing the pack to the next contractor when complete, and so on. The end contractor will upload the completed documentation and witness packs to the client/project document management system.

## Water
TM39: Water meter commissioning checklist
Installation | Yes/No | Comments
Install meter according to serial number and location
Confirm installed parts are in line with manufacturer’s requirements, including meter location in pipework
Provide a local manual drain point to allow water discharge downstream of water meter; this is to be piped to a drain
Communications | Yes/No | Comments
Address meter and commission communications to the head end
From the meter’s LCD display, record the volume as well as the date and time the reading is taken
Check that manual meter readings match those recorded electronically
Set logging to the required interval
Verification | Yes/No | Comments
Verify installation of the water meter
Record the volume and flow rate, along with the date and time the reading is taken
Discharge a suitable volume of water to a drain
Record the volume and flow rate, along with the date and time the reading is taken
Ensure each meter password has been changed from the default settings and documented
Billing | Yes/No | Comments
Commission data transfer from the head end to the billing and analytics system
Validate data passage from meter to billing system
Verification by calculation — do the sub meters add to the main meters? If not, return to the previous steps
Trend review and reporting — do the meter profiles seem sensible? If not, return to the previous steps
Data analytics set up and testing
Revert logging to specified interval
Documentation | Yes/No | Comments
A single coordinated document pack will be used by all trades
Format set by lead contractor; each trade can enhance their section with additional company-specific checklists
The first contractor will start the chain, passing the pack to the next contractor when complete, and so on. The end contractor will upload the completed documentation and witness packs to the client/project document management system.

## Steam
TM39: Steam meter commissioning checklist
Pre-commissioning checks
Verify meter specification | Yes/No | Comments
Confirm the meter type (pressure and/or temperature density compensation)
Check the pressure andtemperature ratings
Confirm the accuracy and turn down of the unit
Inspect meter and accessories | Yes/No | Comments
Check the meter for any physical damage
Verify accessories (temperature and pressure sensing range, connectors) are correct and compatible
Site readiness | Yes/No | Comments
Confirm that the metering location has appropriate steam quality, and appropriate install distance from valves, bends and other ancillaries
The area for an instrument should be clean, dry, and accessible
Ensure that the mounting structure/enclosure is ready and secure
Safety precautions | Yes/No | Comments
Ensure all works are carried out in line with associated RAMS, using all appropriate personnel protective equipment (PPE)
Upstream and downstream double isolation with a proving bleed line is recommended on a steam system. Ensure local instrument power supply disconnect before starting installation
Confirm earthing and bonding arrangements
Installation
Mounting | Yes/No | Comments
Install the meter, with appropriate supporting hardware, in the designated pipework
Ensure the meter and any ancillaries are mounted as intended by manufacturer and supported securely
Pipework | Yes/No | Comments
Consider and install sufficient pipework, up and down stream of the meter
Pressure ratings of pipework, ancillaries and fittings must align with the minimum requirement of the system
Bypass lines, appropriate isolation and proving of isolation should be considered
Wiring | Yes/No | Comments
Connect all signal and earth wires according to wiring diagram
Use appropriate wire sizes and torque specifications
Where possible, connect to the meter using the communication port where steam flow, pressure and temperature can be extracted
Sealing and security | Yes/No | Comments
Label the meter with ID, where possible
Sealing of the meter enclosure, is generally not required, but wiring can be used to prevent tampering
Power up and initial testing
Switch power ON | Yes/No | Comments
Apply power supply to the meter
Check for abnormal signs such as smoke, sparks, or noise
Turning on the steam | Yes/No | Comments
On a steam system, it is very important to gradually bring the system up to temperature and pressure
Instrumentation in the line can be irreversibly damaged if the introduction of pressure happens too quickly
Initial meter check | Yes/No | Comments
Verify the meter display powers up and shows basic parameters
Confirm sensible pressure, temperature and flow readings — if steam is present
Check meter functionality | Yes/No | Comments
Verify energy measurement (kW·h/kg per hour) by applying a known load, if possible
Confirm meter starts recording consumption correctly
Calibration and verification
Calibration | Yes/No | Comments
Steam meters should be calibrated at intervals in keeping with the overriding quality system
For fiscal measurement removal of the device and comparison with a calibrated reference meter is required
Record results | Yes/No | Comments
Document initial readings, test results, and calibration certificates
Commissioning completion
Final Inspection | Yes/No | Comments
Inspect all connections, seals, and labelling
Ensure safety and compliance with relevant standards
Documentation | Yes/No | Comments
Complete commissioning report with meter details, test results, and photos
Ensure each meter password has been changed from the default settings and documented
Handover | Yes/No | Comments
Provide meter information and instructions to the end user or facility manager
Train personnel on meter reading and basic troubleshooting if needed
Post-commissioning
Monitoring | Yes/No | Comments
Monitor meter readings periodically for consistency
Address any anomalies immediately
Routine maintenance | Yes/No | Comments
Schedule periodic inspections and carry out health check of the meter hardware inbuilt systems, if such function exists
Pre-Commissioning Checks
Verify Meter Specification | Confirm the meter type (pressure and/or temperature density compensation).
Check the Pressure and Temperature ratings.
Confirm the accuracy and turn down of the unit.
Inspect Meter and Accessories | Check the meter for any physical damage.
Verify accessories (temperature and pressure sensing range, connectors) are correct and compatible.
Site Readiness | Confirm that the metering location has appropriate steam quality, and appropriate install distance from valves, bends and other ancillaries.
The area for an instrument should be clean, dry, and accessible.
Ensure that the mounting structure/enclosure is ready and secure.
Safety Precautions | Ensure all works are carried out in line with associated RAMS, using all appropriate Personnel Protective Equipment (PPE).
Up and down stream double isolation with a proving bleed line is recommended on a steam system. Ensure local instrument power supply disconnect before starting installation.
Confirm earthing and bonding arrangements.
Installation
Mounting | Install the meter, with appropriate supporting hardware, in the designated pipework.
Ensure the meter and any ancillaries are mounted as intended by manufacturer and supported securely.
Pipe Work | Consider and installation sufficient pipework, up and down stream of the meter.
Pressure ratings of pipework, ancillaries and fittings must align with the minimum requirement of the system.
Bypass lines, appropriate isolation and proving of isolation should be considered
Wiring | Connect all signal and earth wires according to wiring diagram.
Use appropriate wire sizes and torque specifications.
Where possible, connect to the meter using the communication port, where you can extract Steam Flow, Pressure and Temperature
Sealing and Security | Label the meter with ID, where possible.
Sealing of the meter enclosure, is generally not required, but wiring can be used to prevent tampering.
Power Up and Initial Testing
Switch ON Power | Apply power supply to the meter.
Check for abnormal signs such as smoke, sparks, or noise.
Turning on the Steam | On a steam system, it is very important to gradually bring the system up to temperature and pressure.
Instrumentation in the line can be irreversibly damaged if the introduction of pressure happens too quickly.
Initial Meter Check | Verify the meter display powers up and shows basic parameters.
Confirm sensible pressure, temperature and flow readings – if steam is present.
Check Meter Functionality | Verify energy measurement (kWh/kg/hr) by applying a known load, if possible.
Confirm meter starts recording consumption correctly.
Calibration and Verification
Calibration | Steam meters should be calibrated at intervals in keeping with the overriding quality system.
For fiscal measurement removal of the device and comparison with a calibrated reference meter is required.
Record Results | Document initial readings, test results, and calibration certificates.
Commissioning Completion
Final Inspection | Inspect all connections, seals, and labelling.
Ensure safety and compliance with relevant standards.
Documentation | Complete commissioning report with meter details, test results, and photos.
Ensure each meter password has been changed from the default settings and documented.
Handover | Provide meter information and instructions to the end user or facility manager.
Train personnel on meter reading and basic troubleshooting if needed.
Post-Commissioning
Monitoring | Monitor meter readings periodically for consistency.
Address any anomalies immediately.
Routine Maintenance | Schedule periodic inspections and carry out health check of the meter hardware inbuilt systems, if such function exists.