## Data (hidden)
End Use Category |  | Heating | Hot Water | Internal Lighting | Fans & Pumps | Cooling | Lifts | Building Related Services | External Lighting | Small Power | Catering | Total
| Please Select | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC | TBC
School Output Specification DfE Annex 2H: Energy - May 2019 | Primary
| Secondary | 20 | 4 | 13 | 7 | 1 | 1 | 4 | 0 | 25 | 0 | 75
SEN D
Further Education Output Specification DfE Annex 2H: Energy - Nov 2022 | College - Low Tech | 8 | 5 | 8 | 5 | 0 | 1 | 2 | 6 | 10 | 7 | 52
| College - Mid Tech | 8 | 5 | 8 | 5 | 0 | 1 | 2 | 6 | 12 | 7 | 54
| College - High Tech | 8 | 5 | 8 | 5 | 0 | 1 | 2 | 6 | 25 | 7 | 67

## Monthly Totals
End Use Category | Teaching Block
Meter Reference | EM01
Summed Annual Total (MWh) | 280.6164
Month |  | Monthly Total (MWh) | End Use Category (Included within EUI) | [10 empty] | Miscellaneous (Not Included within EUI)
|  |  | Heating | Hot Water | Internal Lighting | Fans & Pumps | Cooling | Lifts | Building Related Services | External Lighting | Small Power | Catering | Server
January |  | 28.1031 | 6.388 | 2.7682 | 2.3129 | 2.3448 | 0.332 | 0.06827 | 2.2756 | 0.1598 | 4.4337 | 3.9824 | 3.0374 | 0
February |  | 23.826 | 4.1192 | 2.4278 | 1.9287 | 1.9322 | 0.3218 | 0.06827 | 2.2756 | 0.1164 | 3.9101 | 3.9824 | 2.7435 | 0
March |  | 21.0363 | 2.3814 | 2.0884 | 1.6856 | 1.6271 | 0.3692 | 0.06827 | 2.2756 | 0.1044 | 3.4165 | 3.9824 | 3.0374 | 0
April |  | 26.2782 | 3.3323 | 3.0268 | 2.4746 | 2.5513 | 0.3932 | 0.06827 | 2.2756 | 0.0541 | 5.1802 | 3.9824 | 2.9394 | 0
May |  | 25.5524 | 1.8883 | 3.0034 | 2.4288 | 3.181 | 0.4613 | 0.06827 | 2.2756 | 0.0339 | 5.192 | 3.9824 | 3.0374 | 0
June |  | 24.6886 | 1.341 | 2.8527 | 2.3083 | 3.5122 | 0.4686 | 0.06827 | 2.2756 | 0.0129 | 4.9272 | 3.9824 | 2.9394 | 0
July |  | 22.4423 | 0.77 | 2.4195 | 1.9386 | 3.2507 | 0.5055 | 0.06827 | 2.2756 | 0.0194 | 4.175 | 3.9824 | 3.0374 | 0
August |  | 10.1447 | 0 | 0.1045 | 0 | 0 | 0.4952 | 0.06827 | 2.2756 | 0.0451 | 0.1362 | 3.9824 | 3.0374 | 0
September |  | 24.3641 | 1.4256 | 2.8504 | 2.3729 | 2.9939 | 0.4613 | 0.06827 | 2.2756 | 0.073 | 4.9213 | 3.9824 | 2.9394 | 0
October |  | 24.101 | 2.0348 | 2.7444 | 2.2966 | 2.4335 | 0.4313 | 0.06827 | 2.2756 | 0.1105 | 4.6862 | 3.9824 | 3.0374 | 0
November |  | 27.0041 | 2.4816 | 3.6115 | 2.9461 | 2.4655 | 0.3921 | 0.06827 | 2.2756 | 0.15 | 5.6916 | 3.9824 | 2.9394 | 0
December |  | 23.0756 | 2.6845 | 2.6073 | 1.9967 | 1.9602 | 0.3624 | 0.06827 | 2.2756 | 0.1848 | 3.9161 | 3.9824 | 3.0374 | 0
Annual Total (MWh) |  | 280.6164 | 28.8467 | 30.5049 | 24.6898 | 28.2526 | 4.9939 | 0.81924 | 27.3072 | 1.0643 | 50.5861 | 47.7888 | 35.7629 | 0

## Heating
End Use Category | Heating
Meter Reference | VM01
Summed Annual Total (MWh) | 28.8467
Meter Reference | EM02 | EM03 | EM04 | EM05 | EM06 | End Use Monthly Total (MWh)
Meter Description | ASHP 1 | ASHP 2 | Ground Floor Overdoor Heaters | Ground Floor Fancoil Units | First Floor Fan Convector
January | 2.7765 | 2.7765 | 0.6246 | 0.0385 | 0.1719 | 6.388
February | 1.7941 | 1.7941 | 0.3896 | 0.0282 | 0.1132 | 4.1192
March | 1.0454 | 1.0454 | 0.2127 | 0.0151 | 0.0628 | 2.3814
April | 1.5216 | 1.5216 | 0.2058 | 0.015 | 0.0682 | 3.3323
May | 0.94415 | 0.94415 | 0 | 0 | 0 | 1.8883
June | 0.6681 | 0.6681 | 0.003 | 0 | 0.0018 | 1.341
July | 0.385 | 0.385 | 0 | 0 | 0 | 0.77
August | 0 | 0 | 0 | 0 | 0 | 0
September | 0.7128 | 0.7128 | 0 | 0 | 0 | 1.4256
October | 0.98195 | 0.98195 | 0.0551 | 0.0051 | 0.0107 | 2.0348
November | 1.1214 | 1.1214 | 0.1852 | 0.015 | 0.0386 | 2.4816
December | 1.1757 | 1.1757 | 0.2515 | 0.0189 | 0.0627 | 2.6845
Meter Annual Total (MWh) | 13.1267 | 13.1267 | 1.9275 | 0.1358 | 0.5299 | 28.8467

## Hot Water
End Use Category | Hot Water
Meter Reference | VM02
Summed Annual Total (MWh) | 30.5049
Meter Reference | EM07 | EM08 | EM09 | EM10 | EM11 | EM12 | End Use Monthly Total (MWh)
Meter Description | Ground Floor Staff Workroom Boiler | First Floor Staff Workroom Boiler | Second Floor Staff Workroom Boiler | Science Water Heaters | Trace Heating | Condensers
January | 0.0256 | 0.0533 | 0.0059 | 0.869 | 0.2042 | 1.6102 | 2.7682
February | 0.0227 | 0.0471 | 0.0052 | 0.7668 | 0.163 | 1.423 | 2.4278
March | 0.0197 | 0.0408 | 0.0045 | 0.6646 | 0.1028 | 1.256 | 2.0884
April | 0.0302 | 0.0628 | 0.007 | 1.0224 | 0.0318 | 1.8726 | 3.0268
May | 0.0302 | 0.0628 | 0.007 | 1.0224 | 0.005 | 1.876 | 3.0034
June | 0.0287 | 0.0596 | 0.0066 | 0.9712 | 0.0026 | 1.784 | 2.8527
July | 0.0242 | 0.0502 | 0.0056 | 0.8178 | 0 | 1.5217 | 2.4195
August | 0 | 0 | 0 | 0 | 0 | 0.1045 | 0.1045
September | 0.0287 | 0.0596 | 0.0066 | 0.9712 | 0.0003 | 1.784 | 2.8504
October | 0.0271 | 0.0564 | 0.0063 | 0.9236 | 0.0107 | 1.7203 | 2.7444
November | 0.0332 | 0.069 | 0.0077 | 1.164 | 0.0521 | 2.2855 | 3.6115
December | 0.0227 | 0.0471 | 0.0052 | 0.7936 | 0.1448 | 1.5939 | 2.6073
Meter Annual Total (MWh) | 0.293 | 0.6087 | 0.0676 | 9.9866 | 0.7173 | 18.8317 | 30.5049

## Internal Lighting
End Use Category | Internal Lighting
Meter Reference | VM03
Summed Annual Total (MWh) | 24.6898
Meter Reference | EM13 | EM14 | EM15 | EM16 | EM17 | End Use Monthly Total (MWh)
Meter Description | Ground Floor General Lighting | Drama General Lighting | First Floor General Lighting | Second Floor General Lighting | Science General Lighting
January | 0.9984 | 0.1656 | 0.5444 | 0.3679 | 0.2366 | 2.3129
February | 0.8348 | 0.1447 | 0.4533 | 0.3091 | 0.1868 | 1.9287
March | 0.7279 | 0.1246 | 0.3975 | 0.271 | 0.1646 | 1.6856
April | 1.0738 | 0.1912 | 0.5804 | 0.4067 | 0.2225 | 2.4746
May | 1.0556 | 0.1898 | 0.5695 | 0.4041 | 0.2098 | 2.4288
June | 1.003 | 0.1799 | 0.5431 | 0.3847 | 0.1976 | 2.3083
July | 0.8432 | 0.1519 | 0.4555 | 0.3232 | 0.1648 | 1.9386
August | 0 | 0 | 0 | 0 | 0 | 0
September | 1.03 | 0.1818 | 0.5566 | 0.388 | 0.2165 | 2.3729
October | 0.9967 | 0.1744 | 0.5376 | 0.3717 | 0.2162 | 2.2966
November | 1.2703 | 0.2122 | 0.6952 | 0.4685 | 0.2999 | 2.9461
December | 0.8587 | 0.1455 | 0.4708 | 0.3185 | 0.2032 | 1.9967
Meter Annual Total (MWh) | 10.6924 | 1.8616 | 5.8039 | 4.0134 | 2.3185 | 24.6898

## Fans & Pumps
End Use Category | Fans & Pumps
Meter Reference | VM04
Summed Annual Total (MWh) | 28.2526
Meter Reference | EM18 | EM19 | EM20 | EM21 | EM22 | EM23 | EM24 | EM25 | EM26 | EM27 | End Use Monthly Total (MWh)
Meter Description | Ground Floor MVHRs | Ground Floor Extract/Supply Fans | First Floor MVHRs | First Floor Extract/Supply Fans | Second Floor MVHRs | Second Floor Extract/Supply Fans | Science MVHRs & Fume Cupboard Fans | LTHW Pumps | DHW Pumps | Kitchen Extract Fan
January | 0.3193 | 0.098 | 0.5574 | 0.011 | 0.2939 | 0.0008 | 0.2814 | 0.66465 | 0.03 | 0.0884 | 2.3448
February | 0.2804 | 0.0782 | 0.4879 | 0.0094 | 0.2579 | 0.0007 | 0.2479 | 0.46535 | 0.0265 | 0.078 | 1.9322
March | 0.2282 | 0.0475 | 0.4093 | 0.0075 | 0.2164 | 0.0006 | 0.2104 | 0.41665 | 0.023 | 0.0676 | 1.6271
April | 0.3881 | 0.0951 | 0.7014 | 0.0128 | 0.3625 | 0.001 | 0.3618 | 0.4893 | 0.0353 | 0.104 | 2.5513
May | 0.5008 | 0.1755 | 0.9686 | 0.0186 | 0.474 | 0.001 | 0.498 | 0.4052 | 0.0353 | 0.104 | 3.181
June | 0.5753 | 0.2749 | 1.0821 | 0.024 | 0.5256 | 0.0009 | 0.5635 | 0.3335 | 0.0336 | 0.0988 | 3.5122
July | 0.5781 | 0.265 | 1.0471 | 0.0233 | 0.5013 | 0.0008 | 0.5406 | 0.18295 | 0.0283 | 0.0832 | 3.2507
August | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 0.4655 | 0.1916 | 0.9188 | 0.019 | 0.4503 | 0.0009 | 0.438 | 0.37745 | 0.0336 | 0.0988 | 2.9939
October | 0.3863 | 0.1 | 0.7161 | 0.0125 | 0.3551 | 0.0009 | 0.3665 | 0.36465 | 0.0379 | 0.0936 | 2.4335
November | 0.3655 | 0.0715 | 0.6618 | 0.0118 | 0.3497 | 0.0011 | 0.3384 | 0.44575 | 0.1056 | 0.1144 | 2.4655
December | 0.2466 | 0.0528 | 0.435 | 0.008 | 0.2351 | 0.0007 | 0.2259 | 0.60605 | 0.072 | 0.078 | 1.9602
Meter Annual Total (MWh) | 4.3341 | 1.4501 | 7.9855 | 0.1579 | 4.0218 | 0.0094 | 4.0724 | 4.7515 | 0.4611 | 1.0088 | 28.2526

## Cooling
End Use Category | Cooling
Meter Reference | N/A
Summed Annual Total (MWh) | 4.9939
Meter Reference | EM28 | End Use Monthly Total (MWh)
Meter Description | Condensers
January | 0.332 | 0.332
February | 0.3218 | 0.3218
March | 0.3692 | 0.3692
April | 0.3932 | 0.3932
May | 0.4613 | 0.4613
June | 0.4686 | 0.4686
July | 0.5055 | 0.5055
August | 0.4952 | 0.4952
September | 0.4613 | 0.4613
October | 0.4313 | 0.4313
November | 0.3921 | 0.3921
December | 0.3624 | 0.3624
Meter Annual Total (MWh) | 4.9939 | 4.9939

## Lifts
End Use Category | Lifts
Meter Reference | N/A
Summed Annual Total (MWh) | 0.81924
Meter Reference | EM29 | End Use Monthly Total (MWh)
Meter Description | Lifts
January | 0.06827 | 0.06827
February | 0.06827 | 0.06827
March | 0.06827 | 0.06827
April | 0.06827 | 0.06827
May | 0.06827 | 0.06827
June | 0.06827 | 0.06827
July | 0.06827 | 0.06827
August | 0.06827 | 0.06827
September | 0.06827 | 0.06827
October | 0.06827 | 0.06827
November | 0.06827 | 0.06827
December | 0.06827 | 0.06827
Meter Annual Total (MWh) | 0.81924 | 0.81924

## Building Related Services
End Use Category | Building Related Services
Meter Reference | N/A
Summed Annual Total (MWh) | 27.3072
Meter Reference | EM30 | End Use Monthly Total (MWh)
Meter Description | General Building Related Services
January | 2.2756 | 2.2756
February | 2.2756 | 2.2756
March | 2.2756 | 2.2756
April | 2.2756 | 2.2756
May | 2.2756 | 2.2756
June | 2.2756 | 2.2756
July | 2.2756 | 2.2756
August | 2.2756 | 2.2756
September | 2.2756 | 2.2756
October | 2.2756 | 2.2756
November | 2.2756 | 2.2756
December | 2.2756 | 2.2756
Meter Annual Total (MWh) | 27.3072 | 27.3072

## External Lighting
End Use Category | External Lighting
Meter Reference | VM05
Summed Annual Total (MWh) | 1.0643
Meter Reference | EM31 | EM32 | End Use Monthly Total (MWh)
Meter Description | Roof External Lighting | Ground Floor External Lighting
January | 0.018 | 0.1418 | 0.1598
February | 0.0131 | 0.1033 | 0.1164
March | 0.0118 | 0.0926 | 0.1044
April | 0.0061 | 0.048 | 0.0541
May | 0.0038 | 0.0301 | 0.0339
June | 0.0015 | 0.0114 | 0.0129
July | 0.0022 | 0.0172 | 0.0194
August | 0.0051 | 0.04 | 0.0451
September | 0.0082 | 0.0648 | 0.073
October | 0.0125 | 0.098 | 0.1105
November | 0.0169 | 0.1331 | 0.15
December | 0.0209 | 0.1639 | 0.1848
Meter Annual Total (MWh) | 0.1201 | 0.9442 | 1.0643

## Small Power
End Use Category | Small Power
Meter Reference | VM06
Summed Annual Total (MWh) | 50.5861
Meter Reference | EM33 | EM34 | EM35 | EM36 | EM37 | EM38 | EM39 | EM40 | EM41 | EM42 | End Use Monthly Total (MWh)
Meter Description | Ground Floor General Power | Plant Room General Power | Resistant Materials Power | Construction Textiles Power | Food Room Power | Drama Power | First Floor General Power | Second Floor General Power | Art Power | Science Power
January | 0.3074 | 0 | 0.3303 | 0.2468 | 0.0748 | 0.2423 | 1.3711 | 0.7538 | 0.3347 | 0.7725 | 4.4337
February | 0.2713 | 0 | 0.2914 | 0.2178 | 0.066 | 0.212 | 1.2097 | 0.665 | 0.2953 | 0.6816 | 3.9101
March | 0.235 | 0 | 0.2526 | 0.1887 | 0.0572 | 0.2114 | 1.0485 | 0.5764 | 0.2559 | 0.5908 | 3.4165
April | 0.3616 | 0 | 0.3886 | 0.2904 | 0.088 | 0.2492 | 1.613 | 0.8868 | 0.3937 | 0.9089 | 5.1802
May | 0.3616 | 0 | 0.3886 | 0.2904 | 0.088 | 0.261 | 1.613 | 0.8868 | 0.3937 | 0.9089 | 5.192
June | 0.3436 | 0 | 0.3692 | 0.2758 | 0.0836 | 0.2429 | 1.5323 | 0.8424 | 0.374 | 0.8634 | 4.9272
July | 0.2893 | 0 | 0.3109 | 0.2323 | 0.0704 | 0.2301 | 1.2904 | 0.7095 | 0.315 | 0.7271 | 4.175
August | 0 | 0 | 0 | 0 | 0 | 0.1362 | 0 | 0 | 0 | 0 | 0.1362
September | 0.3436 | 0 | 0.3692 | 0.2758 | 0.0836 | 0.237 | 1.5323 | 0.8424 | 0.374 | 0.8634 | 4.9213
October | 0.3254 | 0 | 0.3497 | 0.2613 | 0.0792 | 0.2485 | 1.4517 | 0.7981 | 0.3543 | 0.818 | 4.6862
November | 0.3978 | 0 | 0.4274 | 0.3194 | 0.0968 | 0.2676 | 1.7743 | 0.9755 | 0.4331 | 0.9997 | 5.6916
December | 0.2713 | 0 | 0.2914 | 0.2178 | 0.066 | 0.218 | 1.2097 | 0.665 | 0.2953 | 0.6816 | 3.9161
Meter Annual Total (MWh) | 3.5079 | 0 | 3.7693 | 2.8165 | 0.8536 | 2.7562 | 15.646 | 8.6017 | 3.819 | 8.8159 | 50.5861

## Catering
End Use Category | Catering
Meter Reference | N/A
Summed Annual Total (MWh) | 47.7888
Meter Reference | EM43 | End Use Monthly Total (MWh)
Meter Description | Kitchen
January | 3.9824 | 3.9824
February | 3.9824 | 3.9824
March | 3.9824 | 3.9824
April | 3.9824 | 3.9824
May | 3.9824 | 3.9824
June | 3.9824 | 3.9824
July | 3.9824 | 3.9824
August | 3.9824 | 3.9824
September | 3.9824 | 3.9824
October | 3.9824 | 3.9824
November | 3.9824 | 3.9824
December | 3.9824 | 3.9824
Meter Annual Total (MWh) | 47.7888 | 47.7888

## Server
End Use Category | Server
Meter Reference | N/A
Summed Annual Total (MWh) | 35.7629
Meter Reference | EM44 | End Use Monthly Total (MWh)
Meter Description | First Floor Server Room
January | 3.0374 | 3.0374
February | 2.7435 | 2.7435
March | 3.0374 | 3.0374
April | 2.9394 | 2.9394
May | 3.0374 | 3.0374
June | 2.9394 | 2.9394
July | 3.0374 | 3.0374
August | 3.0374 | 3.0374
September | 2.9394 | 2.9394
October | 3.0374 | 3.0374
November | 2.9394 | 2.9394
December | 3.0374 | 3.0374
Meter Annual Total (MWh) | 35.7629 | 35.7629

## Miscellaneous
End Use Category | Miscellaneous (Not Included within EUI)
Meter Reference | VM07
Summed Annual Total (MWh) | 0
Meter Reference | EM45 | End Use Monthly Total (MWh)
Meter Description | Electric Vehicle Charging
January | N/A | 0
February | N/A | 0
March | N/A | 0
April | N/A | 0
May | N/A | 0
June | N/A | 0
July | N/A | 0
August | N/A | 0
September | N/A | 0
October | N/A | 0
November | N/A | 0
December | N/A | 0
Meter Annual Total (MWh) | N/A | 0