## Slide 1
METERING TREE – SCHOOL EXAMPLE
EM
02
ASHP 1
13.127 MWh/yr
EM
03
ASHP 2
13.127 MWh/yr
EM
04
OVERDOOR HEATERS
1.928 MWh/yr
EM
05
FANCOIL UNITS
0.136 MWh/yr
EM
06
FAN CONVECTOR
0.530 MWh/yr
VM
01
28.847 MWh/yr
HEATING
EM
07
GROUND FLOOR
STAFF ROOM BOILER
0.293 MWh/yr
EM
08
FIRST FLOOR
STAFF ROOM BOILER
0.609 MWh/yr
EM
09
SECOND FLOOR
STAFF ROOM BOILER
0.068 MWh/yr
EM
10
SCIENCE WATER HEATERS
9.987 MWh/yr
EM
11
TRACE HEATING
0.717 MWh/yr
VM
02
30.505 MWh/yr
HOT WATER
EM
12
CONDENSORS
18.832 MWh/yr
EM
13
GROUND FLOOR
GENERAL LIGHTING
10.692 MWh/yr
EM
14
DRAMA GENERAL LIGHTING
1.862 MWh/yr
EM
15
FIRST FLOOR
GENERAL LIGHTING
5.804 MWh/yr
EM
16
SECOND FLOOR
GENERAL LIGHTING
4.013 MWh/yr
EM
17
SCIENCE GENERAL LIGHTING
2.319 MWh/yr
VM
03
24.690 MWh/yr
INTERNAL LIGHTING
EM
18
GROUND FLOOR
MVHRS
4.334 MWh/yr
EM
19
GROUND FLOOR
EXTRACT/SUPPLY FANS
1.450 MWh/yr
EM
20
FIRST FLOOR
MVHRS
7.986 MWh/yr
EM
21
FIRST FLOOR
EXTRACT/SUPPLY FANS
0.158 MWh/yr
EM
22
SECOND FLOOR
MVHRS
4.022 MWh/yr
VM
04
28.253 MWh/yr
FANS & PUMPS
EM
23
SECOND FLOOR
EXTRACT/SUPPLY FANS
0.009 MWh/yr
EM
24
SCIENCE MVHRS & FUME CUPBOARD FANS
4.072 MWh/yr
EM
25
LTHW PUMPS
4.752 MWh/yr
EM
26
DHW PUMPS
0.461 MWh/yr
EM
27
KITCHEN EXTRACT FANS
1.009 MWh/yr
EM
28
CONDENSORS
4.994 MWh/yr
4.994 MWh/yr
COOLING
EM
29
LIFTS
0.819 MWh/yr
0.819 MWh/yr
LIFTS
EM
30
GENERAL BUILDING
RELATED SERVICES
27.307 MWh/yr
27.307 MWh/yr
BUILDING RELATED SERVICES
EM
31
ROOF EXTERNAL LIGHTING
0.120 MWh/yr
EM
32
GROUND FLOOR
EXTERNAL LIGHTING
0.944 MWh/yr
VM
05
1.064 MWh/yr
EXTERNAL LIGHTING
EM
33
GROUND FLOOR GENERAL POWER
3.508 MWh/yr
EM
34
PLANT ROOM GENERAL POWER
0 MWh/yr
EM
35
RESISTANT MATERIALS POWER
3.769 MWh/yr
EM
36
CONSTRUCTIONTEXTILES POWER
2.817 MWh/yr
EM
37
FOOD ROOM POWER
0.854 MWh/yr
VM
06
50.586 MWh/yr
SMALL POWER
EM
38
DRAMA POWER
2.756 MWh/yr
EM
39
FIRST FLOOR GENERAL POWER
15.646 MWh/yr
EM
40
SECOND FLOOR GENERAL POWER
8.602 MWh/yr
EM
41
ART POWER
3.819 MWh/yr
EM
42
SCIENCE POWER
8.816 MWh/yr
EM
43
KITCHEN
47.879 MWh/yr
47.789 MWh/yr
CATERING
EM
44
FIRST FLOOR SERVER ROOM
35.763 MWh/yr
35.763 MWh/yr
SERVER
EM
45
ELECTRIC VEHICLE CHARGING
? MWh/yr
? MWh/yr
MISCELLANEOUS
EM
01
280.616 MWh/yr
KEY
= Direct meter
EM
nn
VM
nn
= Virtual meter
TEACHING BLOCK
(NOT INCLUDED WITHIN EUI)