## Elec Strat Overview
Electrical Metering Strategy (DATA Rooms)
Description | Voltage | Meter Designation | Method | Phase | Total Estimate Method 1 (by difference) kWh/year | Calculation For Column F | Total Estimate Method 2 (DB/load & hours run) kWh/year | Lighting End-Use Total (kWh/year) | Data End-Use Total (kWh/year) | AC End-Use Total (kWh/year)
MCCB Panel A (NEW) | 400V AC | EM 1 | Direct Metered | TP&N | 182473 | NA (direct metered) | 182473
Description | Voltage |  |  | Phase |  |  | Estimated consumption per meter (kWh/year)
MCCB Panel C (NEW) | 400V AC | EM 2 | Direct Metered | TP&N | 101008 | NA (direct metered) | 101008
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year)
DB DATA 1 | 230V AC | EM 10 | CALC. by difference | SP&N | 21966 | (EM2-EM3)/4 | 12290 |  | 12290
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year)
DB DATA 2 | 230V AC | EM 11 | CALC. by difference | SP&N | 21966 | (EM2-EM3)/4 | 6044 |  | 6044
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year)
DB DATA 3 | 230V AC | EM 12 | CALC. by difference | SP&N | 21966 | (EM2-EM3)/4 | 14909 |  | 14909
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year)
DB DATA 4 | 400V AC | EM 13 | CALC. by difference | TP&N | 21966 | (EM2-EM3)/4 | 54621 |  | 54621
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year)
DB DATA ROOM | 400V AC | EM 3 | Direct Metered | TP&N | 13144 | NA (direct metered) | 13144
Lighting 1 + External | 230V AC | EM 4 | Direct Metered | SP&N | 173 | NA (direct metered) | 173 | 173
Lighting -1,2,3,4, | 230V AC | EM 5 | Direct Metered | SP&N | 216 | NA (direct metered) | 216 | 216
AC External Unit 1 Ib:20A | 230V AC | EM 6 | CALC. by difference | SP&N | 3188.75 | EM6=[EM3 - (EM4+EM5)]/4 | 3450 |  |  | 3450
AC External Unit 2 Ib:16A | 230V AC | EM 7 | CALC. by difference | SP&N | 3188.75 | EM7=[EM3 - (EM4+EM5)]/4 | 2668 |  |  | 2668
AC External Unit 3 Ib:20A | 230V AC | EM 8 | CALC. by difference | SP&N | 3188.75 | EM8=[EM3 - (EM4+EM5)]/4 | 3220 |  |  | 3220
AC External Unit 4 Ib:20A | 230V AC | EM 9 | CALC. by difference | SP&N | 3188.75 | EM9=[EM3 - (EM4+EM5)]/4 | 3335 |  |  | 3335
Description | Voltage |  |  | Phase |  |  | Estimated consumption per DB/Load (kWh/year) | Total (kWh/year) | Total (kWh/year) | Total (kWh/year)
Distribution Board B (EXISTING) | 400V AC | NA | Direct Metered | TP&N | 80921 | NA (direct metered) | 80921 | 389 | 87864 | 12673
These values are directly metered via physical meters on the DBs.
These values have been determined using the direct metered values, and calculating the other items by difference (formulae in column G).
These values have been calculated based on kW load x hours run.

## Calc H3
DATA ROOMS Client: CIBSE ¦ Revision: 02 ¦ Revision by: XX ¦ Revision date: 07/08/2025
Consumption kWh/year report : Switch Fuse
Company |  |  | Benchmark Electrical Design and Consultancy Ltd
| Description |  |  | Voltage |  |  | Phase | kWh/year
| Switch Fuse |  |  | 400V AC |  |  | TP&N | 182473
Way |  | Description |  |  | kW | Hours/day | Utilisation profile | kWh/year
1.L1,L2,L3 |  | MCCB Panel A (NEW) |  |  | 83.88 | - | - | 182473 | H3

## Calc H3,6,29
DATA ROOMS Client: CIBSE ¦ Revision: 02 ¦ Revision by: XX ¦ Revision date: 07/08/2025
Consumption kWh/year report : MCCB Panel A (NEW)
Company |  |  | Benchmark Electrical Design and Consultancy Ltd
| Description |  |  | Voltage |  |  |  | Phase | kWh/year
| MCCB Panel A (NEW) |  |  | 400V AC |  |  |  | TP&N | 182473 | H3
Way |  | Description |  |  | kW | Hours/day | Days/year | Utilisation profile | kWh/year
1.L1,L2,L3 |  | MCCB Panel C (NEW) |  |  | 27.95 | - |  | - | 101008 | H6
2.L1,L2,L3 |  | Distribution Board B (EXISTING) |  |  | 55.43 | - |  | - | 80921 | H29
3.L1 |  | Tubular heater for kiosk |  |  | 0.5 | 8 | 136 | Tubular Heater | 544
3.L2 |  | SPARE |  |  | 0 | - |  | - | 0
3.L3 |  | SPARE |  |  | 0 | - |  | - | 0
4.L1 |  | SPARE |  |  | 0 | - |  | - | 0
4.L2 |  | SPARE |  |  | 0 | - |  | - | 0
4.L3 |  | SPARE |  |  | 0 | - |  | - | 0
5.L1 |  | SPARE |  |  | 0 | - |  | - | 0
5.L2 |  | SPARE |  |  | 0 | - |  | - | 0
5.L3 |  | SPARE |  |  | 0 | - |  | - | 0
6.L1 |  | SPARE |  |  | 0 | - |  | - | 0
6.L2 |  | SPARE |  |  | 0 | - |  | - | 0
6.L3 |  | SPARE |  |  | 0 | - |  | - | 0
7.L1 |  | SPARE |  |  | 0 | - |  | - | 0
7.L2 |  | SPARE |  |  | 0 | - |  | - | 0
7.L3 |  | SPARE |  |  | 0 | - |  | - | 0

## Calc H6,9,12,15,18,21
DATA ROOMS Client: CIBSE ¦ Revision: 02 ¦ Revision by: XX ¦ Revision date: 07/08/2025
Consumption kWh/year report : MCCB Panel C (NEW)
Company |  |  | Benchmark Electrical Design and Consultancy Ltd
| Description |  |  | Voltage |  |  | Phase | kWh/year
| MCCB Panel C (NEW) |  |  | 400V AC |  |  | TP&N | 101008 | H6
Way |  | Description |  |  | kW | Hours/day | Utilisation profile | kWh/year
1.L1,L2,L3 |  | DB DATA ROOM |  |  | 17.95 | - | - | 13144 | H21
2.L1 |  | DB DATA 1 |  |  | 1.4 | - | - | 12290 | H9
2.L2 |  | DB DATA 2 |  |  | 0.69 | - | - | 6044 | H12
2.L3 |  | DB DATA 3 |  |  | 1.7 | - | - | 14909 | H15
3.L1,L2,L3 |  | DB DATA 4 |  |  | 6.21 | - | - | 54621 | H18
4.L1 |  | SPARE |  |  | 0 | - | - | 0
4.L2 |  | SPARE |  |  | 0 | - | - | 0
4.L3 |  | SPARE |  |  | 0 | - | - | 0

## Calc H21,22,23,24,25,26,27
DATA ROOMS Client: CIBSE ¦ Revision: 02 ¦ Revision by: XX ¦ Revision date: 07/08/2025
Consumption kWh/year report : DB DATA ROOM
Company |  |  | Benchmark Electrical Design and Consultancy Ltd
| Description |  |  | Voltage |  |  |  | Phase | kWh/year
| DB DATA ROOM |  |  | 400V AC |  |  |  | TP&N | 13144 | H21
Way |  | Description |  |  | kW | Hours/day | Days/year | Utilisation profile | kWh/year
1.L1 |  | AC External Unit 1 Ib:20A |  |  | 4.6 | 5 | 150 | AC External Unit | 3450 | H24
1.L2 |  | AC External Unit 2 Ib:16A |  |  | 3.68 | 5 | 145 | AC External Unit | 2668 | H25
1.L3 |  | AC External Unit 3 Ib:20A |  |  | 4.6 | 5 | 140 | AC External Unit | 3220 | H26
2.L1 |  | AC External Unit 4 Ib:20A |  |  | 4.6 | 5 | 145 | AC External Unit | 3335 | H27
2.L2 |  | Lighting 1 + External |  |  | 0.12 | Metered |  | Lighting (Metered) | 173 | H22
2.L3 |  | Lighting -1,2,3,4 |  |  | 0.15 | Metered |  | Lighting (Metered) | 216 | H23
3.L1 |  | SPARE |  |  | 0 | - |  | - | 0
3.L2 |  | SPARE |  |  | 0 | - |  | - | 0
3.L3 |  | FILTER 1AA |  |  | 0.2 | 24 | 135 | Tubular Heater (Days in year:136.07) | 648
4.L1 |  | SPARE |  |  | 0 | - |  | - | 0
4.L2 |  | SPARE |  |  | 0 | - |  | - | 0
4.L3 |  | SPARE |  |  | 0 | - |  | - | 0