## Generic example & notes
Overview | For Guide Notes see below the tables |  |  | Main systems availabilty |  |  |  | Energy unit costs (optional) |  |  |  | Colour key: | Enter data
Name | Example general building |  |  | Hours per day |  | 11 |  | Day pence/kWh |  | 25 |  |  | Select option
Floor area m2 (optional) | 1000 |  |  | Days per week |  | 5.5 |  | Night/Weekend pence/kWh |  | 25 |  |  | Entries formula (or overwrite)
|  |  |  | Weeks per year |  | 52 | [6 empty] | Results formula
ITEM AND | SYSTEM TYPE |  | INSTALLED WATTS OF POWER |  |  |  | AVAILABILITY AND USAGE FACTORS |  |  |  | METERS |  | SUMMARY RESULTS |  |  |  | FURTHER RESULTS | [5 empty] | RESULTS BY ITEM AREA
ITEM NAME | SYSTEM TYPE (select) | NUMBER OF UNITS (eg items, area, persons) | WATTS /UNIT | UNITS USED (select) | HOURS /DAY | DAYS /WEEK | WEEKS /YEAR | Day usage factor % | Night/ Weekend usage factor% | Information source / comment (optional) | Sub meter (optional) (select) | Energy use kWh per year | Energy cost £/year | Percent of total cost | Installed kW | Full load hours/yr | Day kW average | 'Night' kW average | Building W/m2 | Building £/m2 | Building kWh/m2 | Item m2 (if available) can overwrite here | Installed W/ item m2 | kWh/item m2
Office lighting | Lighting | 800 | 5 | W/m2 | 11 | 5.5 | 52 | 70% | 15% | – | – | 12162.8 | 3040.7 | 9.517% | 4 | 3040.7 | 2.8 | 0.6 | 4 | 3.0407 | 12.1628 | 800 | 5 | 15.2035
Receprion lighting | Lighting | 50 | 8 | W/m2 | 11 | 5.5 | 52 | 75% | 5% | – | – | 1055.6 | 263.9 | 0.826% | 0.4 | 2639 | 0.3 | 0.02 | 0.4 | 0.2639 | 1.0556 | 50 | 8 | 21.112
Other lighting | Lighting | 150 | 6 | W/m2 | 11 | 5.5 | 52 | 85% | 5% | – | – | 2658.24 | 664.56 | 2.08% | 0.9 | 2953.6 | 0.765 | 0.045 | 0.9 | 0.66456 | 2.6582 | 150 | 6 | 17.7216
Office equipment | Office equipment | 110 | 80 | W/person | 11 | 5.5 | 52 | 70% | 30% | – | – | 34136.96 | 8534.24 | 26.71% | 8.8 | 3879.2 | 6.16 | 2.64 | 8.8 | 8.5342 | 34.137 | – | – | –
Coffee machines | Catering elecricity | 2 | 1000 | W | 11 | 5.5 | 52 | 40% | 20% | – | – | 4752.8 | 1188.2 | 3.719% | 2 | 2376.4 | 0.8 | 0.4 | 2 | 1.1882 | 4.7528 | – | – | –
Server/comms cabinet | Server / comms / process | 1 | 800 | W | 11 | 5.5 | 52 | 80% | 70% | – | – | 5143.84 | 1285.96 | 4.025% | 0.8 | 6429.8 | 0.64 | 0.56 | 0.8 | 1.286 | 5.1438 | – | – | –
Ceiling AC units | Heating or cooling | 4 | 2200 | W | 11 | 5.5 | 52 | 85% | 5% | – | – | 25991.68 | 6497.92 | 20.34% | 8.8 | 2953.6 | 7.48 | 0.44 | 8.8 | 6.4979 | 25.9917 | – | – | –
Electric heaters | Heating and hot water | 6 | 2000 | W | 11 | 5.5 | 52 | 35% | 5% | – | – | 16567.2 | 4141.8 | 12.96% | 12 | 1380.6 | 4.2 | 0.6 | 12 | 4.1418 | 16.5672 | – | – | –
Supply and extract fans | Fans, pumps, controls | 1 | 2200 | W total | 11 | 5.5 | 52 | 80% | 5% | – | – | 6151.86 | 1537.965 | 4.814% | 2.2 | 2796.3 | 1.76 | 0.11 | 2.2 | 1.538 | 6.1519 | – | – | –
Lifts | Other | 1 | 5000 | W | 11 | 5.5 | 52 | 60% | 15% | – | – | 13630.5 | 3407.625 | 10.67% | 5 | 2726.1 | 3 | 0.75 | 5 | 3.4076 | 13.6305 | – | – | –
External lighting | Other | 5 | 50 | W | 11 | 5.5 | 52 | 10% | 55% | – | – | 847.275 | 211.8187 | 0.663% | 0.25 | 3389.1 | 0.025 | 0.1375 | 0.25 | 0.21182 | 0.84728 | – | – | –
Controls and security | Fans, pumps, controls | 1 | 800 | W | 11 | 5.5 | 52 | 80% | 60% | – | – | 4696.64 | 1174.16 | 3.675% | 0.8 | 5870.8 | 0.64 | 0.48 | 0.8 | 1.1742 | 4.6966 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
TOTAL | [11 empty] | 127795.395 | 31948.8488 | 100% | 45.95 | 2781.1838 | 28.57 | 6.7825 | 45.95 | 31.9488 | 127.7954
[13 empty] | SUMMARY BY SYSTEM TYPE |  |  |  | FURTHER RESULTS BY SYSTEM TYPE
[9 empty] | SYSTEM TYPES (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | (unspecified) |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Heating and hot water |  |  | 16567.2 | 4141.8 | 12.96% | 12 | 1380.6 | 4.2 | 0.6 | 12 | 4.1418 | 16.5672
[9 empty] | Cooling |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Fans, pumps, controls |  |  | 10848.5 | 2712.125 | 8.489% | 3 | 3616.1667 | 2.4 | 0.59 | 3 | 2.7121 | 10.8485
[9 empty] | Lighting |  |  | 15876.64 | 3969.16 | 12.42% | 5.3 | 2995.5925 | 3.865 | 0.665 | 5.3 | 3.9692 | 15.8766
[9 empty] | Office equipment |  |  | 34136.96 | 8534.24 | 26.71% | 8.8 | 3879.2 | 6.16 | 2.64 | 8.8 | 8.5342 | 34.137
[9 empty] | Catering elecricity |  |  | 4752.8 | 1188.2 | 3.719% | 2 | 2376.4 | 0.8 | 0.4 | 2 | 1.1882 | 4.7528
[9 empty] | Other |  |  | 14477.775 | 3619.4437 | 11.33% | 5.25 | 2757.6714 | 3.025 | 0.8875 | 5.25 | 3.6194 | 14.4778
[9 empty] | Server / comms / process |  |  | 5143.84 | 1285.96 | 4.025% | 0.8 | 6429.8 | 0.64 | 0.56 | 0.8 | 1.286 | 5.1438
[9 empty] | Heating or cooling |  |  | 25991.68 | 6497.92 | 20.34% | 8.8 | 2953.6 | 7.48 | 0.44 | 8.8 | 6.4979 | 25.9917
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 127795.395 | 31948.8487 | 100% | 45.95 | 2781.1838 | 28.57 | 6.7825 | 45.95 | 31.9488 | 127.7954
[13 empty] | SUMMARY BY SUB METER |  |  |  | FURTHER RESULTS BY SUB METER
[9 empty] | SUB METERS (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 127795.395 | 31948.8488 | 100% | 45.95 | 2781.1838 | 28.57 | 6.7825 | 45.95 | 31.9488 | 127.7954
[9 empty] | A |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | B |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | C |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | D |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | E |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 127795.395 | 31948.8488 | 100% | 45.95 | 2781.1838 | 28.57 | 6.7825 | 45.95 | 31.9488 | 127.7954
UNIT options (editable)
–
W
W/m2
W total
W/person
Overview | aligned with table column above
The floor area figure is useful but optional. The specific measuremengt type (e.g. Gross or Treated floor area) is also optional.
Main systems availabilty
These three entries are for general system operating times - they are used as the DEFAULT values in the cells below and CAN BE OVERWRITTEN in the cells below
Energy unit cost (optional)
These two entries represent the average unit cost in the 'DAY' operaing preiod and in the 'NIGHT/WEEKENd" period (which is the rest of the year)
ITEM AND | SYSTEM TYPE
ITEM NAME can reflect both the physical zone and the fitting, plant or specific system represented in the rest of the row
SYSTEM TYPE selection is optional - and highly advisable - and is selected from the EDITABLE list in Column K below the data entry
INSTALLED WATTS OF POWER
NUMBER OF UNITS is the 'size' of the item: the number of fittings or the number of square meters of floor area that the item serves
WATTS / UNIT is the installed electrical power of each fitting, or per m2 of floor area served
UNITS USED is selected from the list: Watts, Watts per m2, Watts total. (The list is in rows 101:108 which are ususally hidden rows.)
AVAILABILITY AND USAGE FACTORS
HOURS / DAY is the number of hours that the main building systems operate on a normal working day - it can either be the enabled hours or (if you have it) the width of the "Top Hat" shape of an hourly electricity demand profile.
DAYS / WEEK is normally 5, or 7, or say 5.5 representing some presence on a Saturday
WEEKS / YEAR is normally 52 but a lower value can be appropriate for items that are disabled for part of the year.
Day usage factor % is average 'DAY' period load factor
Night/Weekend usage factor is the load factor during all periods not in the 'DAY' period in the operating weeks.
"Information source / comment (optional)" is free text which can record the source of Watts rating data and the avaiability and usage information.
METERS
Sub meter is an optional entry, selected from an editable list below where the meter totals are all summarised
SUMMARY RESULTS
These are the main annual energy use andenergy cost results, calculated directly from the data entered
FURTHER RESULTS
These results provide insight - for example the Watts per building m2 for an ITEM, or for a SYSTEM TYPE in the table below.
RESULTS BY ITEM AREA
The green cells can be overwritten where the floor area served by an item is known but not used in the data entry
Where avaiable, results expressed 'per item area' are valuable - in contrast to 'per building area'.

## Blank template
Overview |  |  |  | Main systems availabilty |  |  |  | Energy unit costs (optional) |  |  |  | Colour key: | Enter data
Name |  |  |  | Hours per day |  |  |  | Day pence/kWh |  |  |  |  | Select option
Floor area m2 (optional) |  |  |  | Days per week |  |  |  | Night/Wkend pence/kWh |  |  |  |  | Entries formula (or overwrite)
|  |  |  | Weeks per year | [8 empty] | Results formula
ITEM AND | SYSTEM TYPE |  | INSTALLED WATTS OF POWER |  |  |  | AVAILABILITY AND USAGE FACTORS |  |  |  | METERS |  | SUMMARY RESULTS |  |  |  | FURTHER RESULTS | [5 empty] | RESULTS BY ITEM AREA
ITEM NAME | SYSTEM TYPE (select) | NUMBER OF UNITS (eg items, area, persons) | WATTS /UNIT | UNITS USED (select) | HOURS /DAY | DAYS /WEEK | WEEKS /YEAR | Day usage factor % | Night/ Weekend usage factor% | Information source / comment (optional) | Sub meter (optional) (select) | Energy use kWh per year | Energy cost £/year | Percent of total cost | Installed kW | Full load hours/yr | Day kW average | 'Night' kW average | Building W/m2 | Building £/m2 | Building kWh/m2 | Item m2 (if available) can overwrite here | Installed W/ item m2 | kWh/item m2
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
| – |  |  | – | 0 | 0 | 0 |  |  | – | – | 0 | 0 |  | 0 | 0 | 0 | 0 | – | – | – | – | – | –
TOTAL | [11 empty] | 0 | 0 | 0% | 0 |  | 0 | 0 | 0 | – | 0
[13 empty] | SUMMARY BY SYSTEM TYPE |  |  |  | FURTHER RESULTS BY SYSTEM TYPE
[9 empty] | SYSTEM TYPES (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | (unspecified) |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Heating and hot water |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Cooling |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Fans, pumps, controls |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Lighting |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Office equipment |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Catering elecricity |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Other |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Server / comms / process |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Heating or cooling |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Total |  |  | 0 | 0 | 0% | 0 |  | 0 | 0 | 0 | – | 0
[13 empty] | SUMMARY BY SUB METER |  |  |  | FURTHER RESULTS BY SUB METER
[9 empty] | SUB METERS (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | A |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | B |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | C |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | D |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | E |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
[9 empty] | Total |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | – | 0
UNIT options (editable)
–
W
W/m2
W total
W/person
Overview | aligned with table column above
The floor area figure is useful but optional. The specific measuremengt type (e.g. Gross or Treated floor area) is also optional.
Main systems availabilty
These three entries are for general system operating times - they are used as the DEFAULT values in the cells below and CAN BE OVERWRITTEN in the cells below
Energy unit cost (optional)
These two entries represent the average unit cost in the 'DAY' operaing preiod and in the 'NIGHT/WEEKENd" period (which is the rest of the year)
ITEM AND | SYSTEM TYPE
ITEM NAME can reflect both the physical zone and the fitting, plant or specific system represented in the rest of the row
SYSTEM TYPE selection is optional - and highly advisable - and is selected from the EDITABLE list in Column K below the data entry
INSTALLED WATTS OF POWER
NUMBER OF UNITS is the 'size' of the item: the number of fittings or the number of square meters of floor area that the item serves
WATTS / UNIT is the installed electrical power of each fitting, or per m2 of floor area served
UNITS USED is selected from the list: Watts, Watts per m2, Watts total. (The list is in rows 101:108 which are ususally hidden rows.)
AVAILABILITY AND USAGE FACTORS
HOURS / DAY is the number of hours that the main building systems operate on a normal working day - it can either be the enabled hours or (if you have it) the width of the "Top Hat" shape of an hourly electricity demand profile.
DAYS / WEEK is normally 5, or 7, or say 5.5 representing some presence on a Saturday
WEEKS / YEAR is normally 52 but a lower value can be appropriate for items that are disabled for part of the year.
Day usage factor % is average 'DAY' period load factor
Night/Weekend usage factor is the load factor during all periods not in the 'DAY' period in the operating weeks.
"Information source / comment (optional)" is free text which can record the source of Watts rating data and the avaiability and usage information.
METERS
Sub meter is an optional entry, selected from an editable list below where the meter totals are all summarised
SUMMARY RESULTS
These are the main annual energy use andenergy cost results, calculated directly from the data entered
FURTHER RESULTS
These results provide insight - for example the Watts per building m2 for an ITEM, or for a SYSTEM TYPE in the table below.
RESULTS BY ITEM AREA
The green cells can be overwritten where the floor area served by an item is known but not used in the data entry
Where avaiable, results expressed 'per item area' are valuable - in contrast to 'per building area'.

## Office example
Overview |  |  |  | Main systems availabilty |  |  |  | Energy unit costs (optional) |  |  |  | Colour key: | Enter data
Name | Example air conditioned office |  |  | Hours per day |  | 13 |  | Day pence/kWh |  | 25 |  |  | Select option
Floor area m2 (optional) | 3800 |  |  | Days per week |  | 5.5 |  | Night/Wkend pence/kWh |  | 17 |  |  | Entries formula (or overwrite)
|  |  |  | Weeks per year |  | 52 | [6 empty] | Results formula
ITEM AND | SYSTEM TYPE |  | INSTALLED WATTS OF POWER |  |  |  | AVAILABILITY AND USAGE FACTORS |  |  |  | METERS |  | SUMMARY RESULTS |  |  |  | FURTHER RESULTS | [5 empty] | RESULTS BY ITEM AREA
ITEM NAME | SYSTEM TYPE (select) | NUMBER OF UNITS (eg items, area, persons) | WATTS /UNIT | UNITS USED (select) | HOURS /DAY | DAYS /WEEK | WEEKS /YEAR | Day usage factor % | Night/ Weekend usage factor% | Information source / comment (optional) | Sub meter (optional) (select) | Energy use kWh per year | Energy cost £/year | Percent of total cost | Installed kW | Full load hours/yr | Day kW average | 'Night' kW average | Building W/m2 | Building £/m2 | Building kWh/m2 | Item m2 (if available) can overwrite here | Installed W/ item m2 | kWh/item m2
General lighting - offices | Lighting | 2700 | 5 | W/m2 | 11 | 5.5 | 52 | 70% | 15% | – | – | 41049.45 | 9356.7825 | 4.921% | 13.5 | 3040.7 | 9.45 | 2.025 | 3.5526 | 2.4623 | 10.8025 | 2700 | 5 | 15.2035
Supply fan | Fans, pumps, controls | 1 | 32000 | W | 13 | 5.5 | 52 | 80% | 5% | Plate W & schedules | – | 103209.6 | 25160.096 | 13.23% | 32 | 3225.3 | 25.6 | 1.6 | 8.4211 | 6.6211 | 27.1604 | – | – | –
Extract fan | Fans, pumps, controls | 1 | 16000 | W | 13 | 5.5 | 52 | 75% | 5% | Plate W & schedules | – | 48630.4 | 11836.448 | 6.225% | 16 | 3039.4 | 12 | 0.8 | 4.2105 | 3.1149 | 12.7975 | – | – | –
Other fans | Fans, pumps, controls | 1 | 4000 | total | 13 | 5.5 | 52 | 85% | 5% | – | – | 13644.8 | 3330.912 | 1.752% | 4 | 3411.2 | 3.4 | 0.2 | 1.0526 | 0.87656 | 3.5907 | – | – | –
Chilled water primary | Fans, pumps, controls | 2 | 3800 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | A | 25925.12 | 6328.7328 | 3.328% | 7.6 | 3411.2 | 6.46 | 0.38 | 2 | 1.6655 | 6.8224 | – | – | –
Chilled water secondary | Fans, pumps, controls | 1 | 3500 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | A | 11939.2 | 2914.548 | 1.533% | 3.5 | 3411.2 | 2.975 | 0.175 | 0.92105 | 0.76699 | 3.1419 | – | – | –
Chilled water AHU pump | Fans, pumps, controls | 1 | 2300 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | A | 7845.76 | 1915.2744 | 1.007% | 2.3 | 3411.2 | 1.955 | 0.115 | 0.60526 | 0.50402 | 2.0647 | – | – | –
LTHW pumps | Fans, pumps, controls | 1 | 2950 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | – | 10063.04 | 2456.5476 | 1.292% | 2.95 | 3411.2 | 2.5075 | 0.1475 | 0.77632 | 0.64646 | 2.6482 | – | – | –
VT pumps | Fans, pumps, controls | 1 | 2200 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | – | 7504.64 | 1832.0016 | 0.9635% | 2.2 | 3411.2 | 1.87 | 0.11 | 0.57895 | 0.48211 | 1.9749 | – | – | –
LTHW AHU pump | Fans, pumps, controls | 1 | 2800 | W | 13 | 5.5 | 52 | 85% | 5% | Plate W & schedules | – | 9551.36 | 2331.6384 | 1.226% | 2.8 | 3411.2 | 2.38 | 0.14 | 0.73684 | 0.61359 | 2.5135 | – | – | –
Heating primary pumps | Fans, pumps, controls | 1 | 400 | W | 13 | 5.5 | 52 | 85% | 5% | – | – | 1364.48 | 333.0912 | 0.1752% | 0.4 | 3411.2 | 0.34 | 0.02 | 0.10526 | 0.087656 | 0.35907 | – | – | –
Chillers | Cooling | 2 | 41000 | W | 13 | 5.5 | 52 | 35% | 5% | – | A | 127280.4 | 30174.196 | 15.87% | 82 | 1552.2 | 28.7 | 4.1 | 21.5789 | 7.9406 | 33.4948 | – | – | –
Office equipment | Office equipment | 160 | 160 | W/person | 11 | 5.5 | 52 | 70% | 30% | – | – | 99307.52 | 21392.384 | 11.25% | 25.6 | 3879.2 | 17.92 | 7.68 | 6.7368 | 5.6296 | 26.1336 | – | – | –
Server room | Server / comms / process | 1 | 6000 | W | 13 | 5.5 | 52 | 80% | 70% | – | – | 38922 | 8044.452 | 4.231% | 6 | 6487 | 4.8 | 4.2 | 1.5789 | 2.117 | 10.2426 | – | – | –
Server room ac | Server / comms / process | 2 | 2000 | W | 13 | 5.5 | 52 | 50% | 40% | – | – | 15464.8 | 3223.896 | 1.696% | 4 | 3866.2 | 2 | 1.6 | 1.0526 | 0.84839 | 4.0697 | – | – | –
Humidification | Humidification | 5 | 6000 | W | 13 | 5.5 | 52 | 40% | 5% | – | – | 52143 | 12433.59 | 6.539% | 30 | 1738.1 | 12 | 1.5 | 7.8947 | 3.272 | 13.7218 | – | – | –
Vending | Catering elecricity | 6 | 500 | W | 13 | 5.5 | 52 | 40% | 20% | – | – | 7472.4 | 1627.236 | 0.8558% | 3 | 2490.8 | 1.2 | 0.6 | 0.78947 | 0.42822 | 1.9664 | – | – | –
Kitchen catering | Catering elecricity | 30 | 400 | W/meal/day | 13 | 5.5 | 52 | 60% | 10% | – | – | 32791.2 | 7716.072 | 4.058% | 12 | 2732.6 | 7.2 | 1.2 | 3.1579 | 2.0305 | 8.6293 | – | – | –
External lighting | Other | 40 | 20 | W | 13 | 5.5 | 52 | 10% | 55% | – | – | 2505.36 | 449.7064 | 0.2365% | 0.8 | 3131.7 | 0.08 | 0.44 | 0.21053 | 0.11834 | 0.65931 | – | – | –
Trace heating | Heating and hot water | 1 | 5000 | W | 13 | 5.5 | 52 | 90% | 20% | – | – | 21749 | 5035.81 | 2.648% | 5 | 4349.8 | 4.5 | 1 | 1.3158 | 1.3252 | 5.7234 | – | – | –
Lifts | Other | 2 | 18000 | W | 13 | 5.5 | 52 | 60% | 15% | – | – | 107406 | 24683.724 | 12.98% | 36 | 2983.5 | 21.6 | 5.4 | 9.4737 | 6.4957 | 28.2647 | – | – | –
Telecoms | Other | 1 | 600 | W | 13 | 5.5 | 52 | 90% | 70% | – | – | 4115.28 | 860.2152 | 0.4524% | 0.6 | 6858.8 | 0.54 | 0.42 | 0.15789 | 0.22637 | 1.083 | – | – | –
Electric heaters | Heating and hot water | 6 | 2000 | W | 13 | 5.5 | 26 | 50% | 15% | – | – | 15670.2 | 3556.254 | 1.87% | 12 | 1305.85 | 6 | 1.8 | 3.1579 | 0.93586 | 4.1237 | – | – | –
Dispatch | Office equipment | 3 | 500 | W | 13 | 5.5 | 52 | 90% | 30% | – | – | 7277.4 | 1638.702 | 0.8618% | 1.5 | 4851.6 | 1.35 | 0.45 | 0.39474 | 0.43124 | 1.9151 | – | – | –
Controls and security | Fans, pumps, controls | 1 | 1200 | W | 13 | 5.5 | 52 | 80% | 60% | – | – | 7182.24 | 1506.5232 | 0.7923% | 1.2 | 5985.2 | 0.96 | 0.72 | 0.31579 | 0.39645 | 1.8901 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 13 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
TOTAL | [11 empty] | 820014.65 | 190138.8333 | 100% | 306.95 | 2671.4926 | 177.7875 | 36.8225 | 80.7763 | 50.0365 | 215.7933
[13 empty] | SUMMARY BY SYSTEM TYPE |  |  |  | FURTHER RESULTS BY SYSTEM TYPE
[9 empty] | SYSTEM TYPES (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | (unspecified) |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Heating and hot water |  |  | 37419.2 | 8592.064 | 4.519% | 17 | 2201.1294 | 10.5 | 2.8 | 4.4737 | 2.2611 | 9.8472
[9 empty] | Cooling |  |  | 127280.4 | 30174.196 | 15.87% | 82 | 1552.2 | 28.7 | 4.1 | 21.5789 | 7.9406 | 33.4948
[9 empty] | Fans, pumps, controls |  |  | 246860.64 | 59945.8132 | 31.53% | 74.95 | 3293.671 | 60.4475 | 4.4075 | 19.7237 | 15.7752 | 64.9633
[9 empty] | Lighting |  |  | 41049.45 | 9356.7825 | 4.921% | 13.5 | 3040.7 | 9.45 | 2.025 | 3.5526 | 2.4623 | 10.8025
[9 empty] | Office equipment |  |  | 106584.92 | 23031.086 | 12.11% | 27.1 | 3933.0229 | 19.27 | 8.13 | 7.1316 | 6.0608 | 28.0487
[9 empty] | Catering elecricity |  |  | 40263.6 | 9343.308 | 4.914% | 15 | 2684.24 | 8.4 | 1.8 | 3.9474 | 2.4588 | 10.5957
[9 empty] | Other |  |  | 114026.64 | 25993.6456 | 13.67% | 37.4 | 3048.8406 | 22.22 | 6.26 | 9.8421 | 6.8404 | 30.007
[9 empty] | Server / comms / process |  |  | 54386.8 | 11268.348 | 5.926% | 10 | 5438.68 | 6.8 | 5.8 | 2.6316 | 2.9654 | 14.3123
[9 empty] | Humidification |  |  | 52143 | 12433.59 | 6.539% | 30 | 1738.1 | 12 | 1.5 | 7.8947 | 3.272 | 13.7218
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 820014.65 | 190138.8333 | 100% | 306.95 | 2671.4926 | 177.7875 | 36.8225 | 80.7763 | 50.0365 | 215.7933
[13 empty] | SUMMARY BY SUB METER |  |  |  | FURTHER RESULTS BY SUB METER
[9 empty] | SUB METERS (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 647024.17 | 148806.0821 | 78.26% | 211.55 | 3058.4929 | 137.6975 | 32.0525 | 55.6711 | 39.1595 | 170.2695
[9 empty] | A |  |  | 172990.48 | 41332.7512 | 21.74% | 95.4 | 1813.3174 | 40.09 | 4.77 | 25.1053 | 10.877 | 45.5238
[9 empty] | B |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | C |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | D |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | E |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 820014.65 | 190138.8333 | 100% | 306.95 | 2671.4926 | 177.7875 | 36.8225 | 80.7763 | 50.0365 | 215.7933
UNIT options (editable)
–
W
W/m2
W total
W/person
Overview | aligned with table column above
The floor area figure is useful but optional. The specific measuremengt type (e.g. Gross or Treated floor area) is also optional.
Main systems availabilty
These three entries are for general system operating times - they are used as the DEFAULT values in the cells below and CAN BE OVERWRITTEN in the cells below
Energy unit cost (optional)
These two entries represent the average unit cost in the 'DAY' operaing preiod and in the 'NIGHT/WEEKENd" period (which is the rest of the year)
ITEM AND | SYSTEM TYPE
ITEM NAME can reflect both the physical zone and the fitting, plant or specific system represented in the rest of the row
SYSTEM TYPE selection is optional - and highly advisable - and is selected from the EDITABLE list in Column K below the data entry
INSTALLED WATTS OF POWER
NUMBER OF UNITS is the 'size' of the item: the number of fittings or the number of square meters of floor area that the item serves
WATTS / UNIT is the installed electrical power of each fitting, or per m2 of floor area served
UNITS USED is selected from the list: Watts, Watts per m2, Watts total. (The list is in rows 101:108 which are ususally hidden rows.)
AVAILABILITY AND USAGE FACTORS
HOURS / DAY is the number of hours that the main building systems operate on a normal working day - it can either be the enabled hours or (if you have it) the width of the "Top Hat" shape of an hourly electricity demand profile.
DAYS / WEEK is normally 5, or 7, or say 5.5 representing some presence on a Saturday
WEEKS / YEAR is normally 52 but a lower value can be appropriate for items that are disabled for part of the year.
Day usage factor % is average 'DAY' period load factor
Night/Weekend usage factor is the load factor during all periods not in the 'DAY' period in the operating weeks.
"Information source / comment (optional)" is free text which can record the source of Watts rating data and the avaiability and usage information.
METERS
Sub meter is an optional entry, selected from an editable list below where the meter totals are all summarised
SUMMARY RESULTS
These are the main annual energy use andenergy cost results, calculated directly from the data entered
FURTHER RESULTS
These results provide insight - for example the Watts per building m2 for an ITEM, or for a SYSTEM TYPE in the table below.
RESULTS BY ITEM AREA
The green cells can be overwritten where the floor area served by an item is known but not used in the data entry
Where avaiable, results expressed 'per item area' are valuable - in contrast to 'per building area'.

## Light industrial example
Overview |  |  |  | Main systems availabilty |  |  |  | Energy unit cost (optional) |  |  |  | Colour key: | Enter data
Name | Example light industrial building |  |  | Hours per day |  | 11 |  | Day pence/kWh |  | 25 |  |  | Select option
Floor area m2 (optional) | 4600 |  |  | Days per week |  | 5.5 |  | Night/Weekend pence/kWh |  | 25 |  |  | Entries formula (or overwrite)
|  |  |  | Weeks per year |  | 52 | [6 empty] | Results formula
ITEM AND | SYSTEM TYPE |  | INSTALLED WATTS OF POWER |  |  |  | AVAILABILITY AND USAGE FACTORS |  |  |  | METERS |  | SUMMARY RESULTS |  |  |  | FURTHER RESULTS | [5 empty] | RESULTS BY ITEM AREA
ITEM NAME | SYSTEM TYPE (select) | NUMBER OF UNITS (eg items, area, persons) | WATTS /UNIT | UNITS USED (select) | HOURS /DAY | DAYS /WEEK | WEEKS /YEAR | Day usage factor % | Night/ Weekend usage factor% | Information source / comment (optional) | Sub meter (optional) (select) | Energy use kWh per year | Energy cost £/year | Percent of total cost | Installed kW | Full load hours/yr | Day kW average | 'Night' kW average | Building W/m2 | Building £/m2 | Building kWh/m2 | Item m2 (if available) can overwrite here | Installed W/ item m2 | kWh/item m2
Lighting, office | Lighting | 1300 | 5 | W/m2 | 11 | 5.5 | 52 | 60% | 10% | – | Office | 15902.9 | 3975.725 | 4.867% | 6.5 | 2446.6 | 3.9 | 0.65 | 1.413 | 0.86429 | 3.4572 | 1300 | 5 | 12.233
Lighting, labs | Lighting | 400 | 7 | W/m2 | 11 | 5.5 | 52 | 85% | 15% | – | Office | 9835.28 | 2458.82 | 3.01% | 2.8 | 3512.6 | 2.38 | 0.42 | 0.6087 | 0.53453 | 2.1381 | 400 | 7 | 24.5882
Lighting, warehouse | Lighting | 1700 | 4 | W/m2 | 11 | 5.5 | 52 | 100% | 5% | – | Warehouse | 23293.4 | 5823.35 | 7.129% | 6.8 | 3425.5 | 6.8 | 0.34 | 1.4783 | 1.2659 | 5.0638 | 1700 | 4 | 13.702
Lighting, demonstration | Lighting | 110 | 10 | W/m2 | 11 | 5.5 | 52 | 60% | 10% | – | – | 2691.26 | 672.815 | 0.8236% | 1.1 | 2446.6 | 0.66 | 0.11 | 0.23913 | 0.14626 | 0.58506 | 110 | 10 | 24.466
Lighting, other | Lighting | 1090 | 5 | W/m2 | 11 | 5.5 | 52 | 60% | 15% | – | – | 14857.245 | 3714.3113 | 4.547% | 5.45 | 2726.1 | 3.27 | 0.8175 | 1.1848 | 0.80746 | 3.2298 | 1090 | 5 | 13.6305
AHUs 1-7 | Fans, pumps, controls | 1 | 7200 | total | 15 | 5.5 | 52 | 100% | 15% | Plate W & schedules | Production | 35689.68 | 8922.42 | 10.92% | 7.2 | 4956.9 | 7.2 | 1.08 | 1.5652 | 1.9397 | 7.7586 | – | – | –
Coffee machines | Catering elecricity | 2 | 2000 | W | 11 | 5.5 | 52 | 15% | 0% | – | – | 1887.6 | 471.9 | 0.5777% | 4 | 471.9 | 0.6 | 0 | 0.86957 | 0.10259 | 0.41035 | – | – | –
Small power, offices | Office equipment | 1300 | 12 | W/m2 | 11 | 5.5 | 52 | 40% | 20% | – | Office | 37071.84 | 9267.96 | 11.35% | 15.6 | 2376.4 | 6.24 | 3.12 | 3.3913 | 2.0148 | 8.0591 | 1300 | 12 | 28.5168
Small power, labs | Server / comms / process | 400 | 25 | W/m2 | 11 | 5.5 | 52 | 60% | 30% | – | Production | 35646 | 8911.5 | 10.91% | 10 | 3564.6 | 6 | 3 | 2.1739 | 1.9373 | 7.7491 | 400 | 25 | 89.115
Cassettes, conference | Cooling | 2 | 2000 | W | 11 | 5.5 | 26 | 25% | 5% | – | Office | 2132 | 533 | 0.6525% | 4 | 533 | 1 | 0.2 | 0.86957 | 0.11587 | 0.46348 | – | – | –
Cassettes, MD | Cooling | 2 | 2200 | W | 11 | 5.5 | 26 | 48% | 5% | – | Office | 3937.076 | 984.269 | 1.205% | 4.4 | 894.79 | 2.112 | 0.22 | 0.95652 | 0.21397 | 0.85589 | – | – | –
Cassettes, computer room | Server / comms / process | 2 | 5000 | W | 11 | 5.5 | 52 | 40% | 25% | – | – | 26559 | 6639.75 | 8.128% | 10 | 2655.9 | 4 | 2.5 | 2.1739 | 1.4434 | 5.7737 | – | – | –
AC unit, workshop | Cooling | 1 | 4000 | W | 11 | 5.5 | 26 | 45% | 5% | – | Production | 3390.4 | 847.6 | 1.038% | 4 | 847.6 | 1.8 | 0.2 | 0.86957 | 0.18426 | 0.73704 | – | – | –
Hot water local | Heating and hot water | 2 | 6000 | W | 11 | 5.5 | 52 | 20% | 0% | – | Office | 7550.4 | 1887.6 | 2.311% | 12 | 629.2 | 2.4 | 0 | 2.6087 | 0.41035 | 1.6414 | – | – | –
Catering incl d/washer | Catering elecricity | 50 | 200 | W/meal/day | 11 | 5.5 | 52 | 40% | 0% | – | – | 12584 | 3146 | 3.851% | 10 | 1258.4 | 4 | 0 | 2.1739 | 0.68391 | 2.7357 | – | – | –
Office server | Server / comms / process | 1 | 1500 | W | 11 | 5.5 | 52 | 70% | 50% | – | Office | 7495.8 | 1873.95 | 2.294% | 1.5 | 4997.2 | 1.05 | 0.75 | 0.32609 | 0.40738 | 1.6295 | – | – | –
Server R&D | Server / comms / process | 1 | 1200 | W | 11 | 5.5 | 52 | 70% | 50% | – | Production | 5996.64 | 1499.16 | 1.835% | 1.2 | 4997.2 | 0.84 | 0.6 | 0.26087 | 0.3259 | 1.3036 | – | – | –
Kitchen extracts | Fans, pumps, controls | 1 | 500 | W | 11 | 5.5 | 26 | 30% | 0% | – | – | 235.95 | 58.9875 | 0.07221% | 0.5 | 471.9 | 0.15 | 0 | 0.1087 | 0.012823 | 0.051293 | – | – | –
Door heater units | Heating and hot water | 3 | 3000 | W | 11 | 5.5 | 52 | 80% | 0% | – | – | 22651.2 | 5662.8 | 6.932% | 9 | 2516.8 | 7.2 | 0 | 1.9565 | 1.231 | 4.9242 | – | – | –
Toilet fans | Fans, pumps, controls | 2 | 200 | W | 11 | 5.5 | 52 | 80% | 0% | – | – | 1006.72 | 251.68 | 0.3081% | 0.4 | 2516.8 | 0.32 | 0 | 0.086957 | 0.054713 | 0.21885 | – | – | –
Room extracts | Fans, pumps, controls | 5 | 200 | W | 11 | 5.5 | 52 | 80% | 0% | – | – | 2516.8 | 629.2 | 0.7702% | 1 | 2516.8 | 0.8 | 0 | 0.21739 | 0.13678 | 0.54713 | – | – | –
Warehouse, heaters | Fans, pumps, controls | 2 | 3000 | W | 11 | 5.5 | 26 | 50% | 15% | – | Warehouse | 7234.5 | 1808.625 | 2.214% | 6 | 1205.75 | 3 | 0.9 | 1.3043 | 0.39318 | 1.5727 | – | – | –
Warehouse, door units | Heating and hot water | 2 | 2000 | W | 11 | 5.5 | 26 | 50% | 15% | – | Warehouse | 4823 | 1205.75 | 1.476% | 4 | 1205.75 | 2 | 0.6 | 0.86957 | 0.26212 | 1.0485 | – | – | –
Warehouse extracts | Fans, pumps, controls | 2 | 1000 | W | 11 | 5.5 | 52 | 50% | 15% | – | – | 4823 | 1205.75 | 1.476% | 2 | 2411.5 | 1 | 0.3 | 0.43478 | 0.26212 | 1.0485 | – | – | –
Heating pumps | Fans, pumps, controls | 1 | 150 | W | 11 | 5.5 | 52 | 80% | 15% | – | – | 503.295 | 125.8238 | 0.154% | 0.15 | 3355.3 | 0.12 | 0.0225 | 0.032609 | 0.027353 | 0.10941 | – | – | –
HVAC controls | Fans, pumps, controls | 1 | 1000 | total | 11 | 5.5 | 52 | 80% | 30% | – | – | 4193.8 | 1048.45 | 1.283% | 1 | 4193.8 | 0.8 | 0.3 | 0.21739 | 0.22792 | 0.9117 | – | – | –
Telecomms | Other | 2 | 300 | W | 11 | 5.5 | 52 | 60% | 30% | – | Office | 2138.76 | 534.69 | 0.6545% | 0.6 | 3564.6 | 0.36 | 0.18 | 0.13043 | 0.11624 | 0.46495 | – | – | –
External lights | Lighting | 3 | 75 | W | 11 | 5.5 | 52 | 15% | 45% | – | – | 672.165 | 168.0412 | 0.2057% | 0.225 | 2987.4 | 0.03375 | 0.10125 | 0.048913 | 0.036531 | 0.14612 | – | – | –
Process heater | Server / comms / process | 1 | 5000 | W | 11 | 5.5 | 52 | 40% | 0% | – | Production | 6292 | 1573 | 1.926% | 5 | 1258.4 | 2 | 0 | 1.087 | 0.34196 | 1.3678 | – | – | –
Other rigs | Server / comms / process | 3 | 3000 | W | 11 | 5.5 | 52 | 50% | 0% | – | Production | 14157 | 3539.25 | 4.333% | 9 | 1573 | 4.5 | 0 | 1.9565 | 0.7694 | 3.0776 | – | – | –
Lighting mezzanine | Lighting | 350 | 7 | W/m2 | 11 | 5.5 | 52 | 90% | 15% | – | – | 8991.255 | 2247.8137 | 2.752% | 2.45 | 3669.9 | 2.205 | 0.3675 | 0.53261 | 0.48866 | 1.9546 | 350 | 7 | 25.6893
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
| – |  |  | – | 11 | 5.5 | 52 |  |  | – | – | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | – | – | –
TOTAL | [11 empty] | 326759.966 | 81689.9915 | 100% | 147.875 | 2209.7039 | 78.7407 | 16.7788 | 32.1467 | 17.7587 | 71.0348
[13 empty] | SUMMARY BY SYSTEM TYPE |  |  |  | FURTHER RESULTS BY SYSTEM TYPE
[9 empty] | SYSTEM TYPES (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | (unspecified) |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Heating and hot water |  |  | 35024.6 | 8756.15 | 10.72% | 25 | 1400.984 | 11.6 | 0.6 | 5.4348 | 1.9035 | 7.614
[9 empty] | Cooling |  |  | 9459.476 | 2364.869 | 2.895% | 12.4 | 762.861 | 4.912 | 0.62 | 2.6957 | 0.5141 | 2.0564
[9 empty] | Fans, pumps, controls |  |  | 56203.745 | 14050.9363 | 17.2% | 18.25 | 3079.6573 | 13.39 | 2.6025 | 3.9674 | 3.0546 | 12.2182
[9 empty] | Lighting |  |  | 76243.505 | 19060.8763 | 23.33% | 25.325 | 3010.6024 | 19.2488 | 2.8063 | 5.5054 | 4.1437 | 16.5747
[9 empty] | Office equipment |  |  | 37071.84 | 9267.96 | 11.35% | 15.6 | 2376.4 | 6.24 | 3.12 | 3.3913 | 2.0148 | 8.0591
[9 empty] | Catering elecricity |  |  | 14471.6 | 3617.9 | 4.429% | 14 | 1033.6857 | 4.6 | 0 | 3.0435 | 0.7865 | 3.146
[9 empty] | Other |  |  | 2138.76 | 534.69 | 0.6545% | 0.6 | 3564.6 | 0.36 | 0.18 | 0.13043 | 0.11624 | 0.46495
[9 empty] | Server / comms / process |  |  | 96146.44 | 24036.61 | 29.42% | 36.7 | 2619.794 | 18.39 | 6.85 | 7.9783 | 5.2253 | 20.9014
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 326759.966 | 81689.9915 | 100% | 147.875 | 2209.7039 | 78.7408 | 16.7788 | 32.1467 | 17.7587 | 71.0348
[13 empty] | SUMMARY BY SUB METER |  |  |  | FURTHER RESULTS BY SUB METER
[9 empty] | SUB METERS (editable) |  |  | kWh/yr | £/year | Percent | Installed kW | Full load hour /year | Day ave kW | Night' ave kW | Building W/m2 | Building £/m2 | Building kWh/m2
[9 empty] | – |  |  | 104173.29 | 26043.3225 | 31.88% | 47.275 | 2203.5598 | 25.1588 | 4.5187 | 10.2772 | 5.6616 | 22.6464
[9 empty] | Production |  |  | 101171.72 | 25292.93 | 30.96% | 36.4 | 2779.4429 | 22.34 | 4.88 | 7.913 | 5.4985 | 21.9939
[9 empty] | Office |  |  | 86064.056 | 21516.014 | 26.34% | 47.4 | 1815.6974 | 19.442 | 5.54 | 10.3043 | 4.6774 | 18.7096
[9 empty] | Warehouse |  |  | 35350.9 | 8837.725 | 10.82% | 16.8 | 2104.2202 | 11.8 | 1.84 | 3.6522 | 1.9212 | 7.685
[9 empty] | D |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | E |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Total |  |  | 326759.966 | 81689.9915 | 100% | 147.875 | 2209.7039 | 78.7408 | 16.7787 | 32.1467 | 17.7587 | 71.0348
UNIT options (editable)
–
W
W/m2
W total
W/person
Overview | aligned with table column above
The floor area figure is useful but optional. The specific measuremengt type (e.g. Gross or Treated floor area) is also optional.
Main systems availabilty
These three entries are for general system operating times - they are used as the DEFAULT values in the cells below and CAN BE OVERWRITTEN in the cells below
Energy unit cost (optional)
These two entries represent the average unit cost in the 'DAY' operaing preiod and in the 'NIGHT/WEEKENd" period (which is the rest of the year)
ITEM AND | SYSTEM TYPE
ITEM NAME can reflect both the physical zone and the fitting, plant or specific system represented in the rest of the row
SYSTEM TYPE selection is optional - and highly advisable - and is selected from the EDITABLE list in Column K below the data entry
INSTALLED WATTS OF POWER
NUMBER OF UNITS is the 'size' of the item: the number of fittings or the number of square meters of floor area that the item serves
WATTS / UNIT is the installed electrical power of each fitting, or per m2 of floor area served
UNITS USED is selected from the list: Watts, Watts per m2, Watts total. (The list is in rows 101:108 which are ususally hidden rows.)
AVAILABILITY AND USAGE FACTORS
HOURS / DAY is the number of hours that the main building systems operate on a normal working day - it can either be the enabled hours or (if you have it) the width of the "Top Hat" shape of an hourly electricity demand profile.
DAYS / WEEK is normally 5, or 7, or say 5.5 representing some presence on a Saturday
WEEKS / YEAR is normally 52 but a lower value can be appropriate for items that are disabled for part of the year.
Day usage factor % is average 'DAY' period load factor
Night/Weekend usage factor is the load factor during all periods not in the 'DAY' period in the operating weeks.
"Information source / comment (optional)" is free text which can record the source of Watts rating data and the avaiability and usage information.
METERS
Sub meter is an optional entry, selected from an editable list below where the meter totals are all summarised
SUMMARY RESULTS
These are the main annual energy use andenergy cost results, calculated directly from the data entered
FURTHER RESULTS
These results provide insight - for example the Watts per building m2 for an ITEM, or for a SYSTEM TYPE in the table below.
RESULTS BY ITEM AREA
The green cells can be overwritten where the floor area served by an item is known but not used in the data entry
Where avaiable, results expressed 'per item area' are valuable - in contrast to 'per building area'.

## Q&A
Q & A
DemRed version m1222. Copyright John Field 2025. Free for use at the user's risk.
Q01 | How do I get started?
The quickest way is to edit the Generic example, or one of the more detailed examples.
To edit an example you can overwrite (or delete) yellow input cells, or where there is a menu select one option.
You could also start from scratch using the Blank template tab. You can copy whole rows from another tab.
Q02 | Where are the guidance notes?
They are below the data and results rows in the 'Generic example & notes' tab - they align with the relevant column.
Try End-down or Cmd-down from a cell to get to its Guide Note.
Q03 | Can I rename, copy or delete a whole tab?
Yes. You can keep all your buildings in one workbook, or all versions of a building.
Q04 | What happens if I want to add more rows?
First see if you can unhide any rows that have been hidden for simpler cases - this may provide enough rows.
After that you can drag-copy whole rows. Or insert new rows then copy whole rows and paste in.
Q05 | What if I need to move a row up or down the table?
You can copy-drag a whole row (or copy and paste it). Or a set of rows.
Q06 | Can I overwrite a blue results cell?
Yes. If you know an item's annual energy use you can overwrite the kWh formula but…
It is preferable to change yellow cells to give the required metered energy. That keeps better consistency with other results.
Q07 | How do I evaluate the demand reduction effect of energy saving actions or measures?
Make a copy in this workbook of the tab you are working on. Then in the new tab make the changes for an energy action or measure.
Repeat for subsequent measures. Tabulate the changed energy uses and obtain the effect of each of the measures as differences.